Table of Contents

# Cisco Secure Workload — IEC 62443 Compliance Framework

## Reference Design | Industrial Automation & Control Systems (IACS)

Version: 1.0
Use Case: Fresh Install, Hybrid Environment (On-Prem + Cloud)
Standards anchor: IEC 62443-3-3 (System security requirements and security levels); IEC 62443-2-1 (Security program requirements for IACS asset owners) — consult your SL-T target and zone/conduit documentation for authoritative control text.

## Reader's Guide

Who this is for. IACS asset owners, OT/IT security architects, plant or operations cybersecurity teams, and integrators preparing for IEC 62443-aligned assessments, customer security requirements, or internal security management system (SMS) evidence for industrial environments.

Scope boundary you must understand before reading further. Cisco Secure Workload (CSW) enforces segmentation, discovers dependencies, and produces forensic telemetry on servers, virtual machines, containers, and cloud workloads — the IT side of the IT/OT boundary and the systems that support IACS (jump hosts, engineering workstations, historians, MES interfaces, DMZ brokers, identity services, patch servers, vendor remote-access concentrators). CSW does not replace dedicated OT visibility for Level 0–2 devices (PLCs, RTUs, IEDs, drives, field instruments). Pair CSW at the IT layer with Cisco Cyber Vision, Claroty, Nozomi, or equivalent for asset discovery, ICS protocol analytics, and device-level integrity signals.

Questions this reference design helps you answer:

- SR 5.1–5.4 (restricted data flow / zones & conduits): Can I prove that only documented conduits carry traffic between OT-support tiers and corporate/cloud, and that lateral movement outside those conduits is structurally denied or logged?

- SR 1.1–1.13 (identification / authentication / access control): Can I show identity-aligned allow rules and deny-by-default paths for systems that administer or bridge into IACS zones?

- SR 3.1–3.9 (data / system integrity): Can I baseline inventory (processes, binaries, listening services) and detect unexpected change or unauthorized software on IACS-adjacent IT workloads?

- SR 6.1–6.2 (event monitoring & timely response): Can I reconstruct a timeline of flows and processes during an OT-adjacent incident?

- SR 7.1–7.8 (resource availability): Can I detect volumetric or connection storms indicative of denial-of-service against critical IT services that underpin OT availability?

- IEC 62443-2-1 (security program / operations): Can I produce continuous monitoring dashboards and exports that feed our SMS without manual spreadsheet reconciliation?

What you'll need. Your zone & conduit model (per IEC 62443-3-2 or customer ZCRD), Security Level Target (SL-T) per zone, inventory of IACS-adjacent IT systems (EWS, jump hosts, AD/PKI, historians), change management approval for sensor install, and naming alignment between your PAS/OT tools and CMDB labels.

Where to start. Sections 1–2 while scoping; 3–5 during pilot sensor and baseline; 6–8 when designing enforcement; 9–10 for control mapping and SMS reporting; section Boundaries before promising CSW coverage to integrators or auditors.

## CSW primer — if you are new to Cisco Secure Workload

Cisco Secure Workload (CSW) is a workload protection platform. A lightweight agent on each server/VM/container observes processes and network flows; cloud connectors add AWS/Azure/GCP inventory where agents are not deployed.

| CSW term | Meaning | Why compliance teams care |
| --- | --- | --- |
| Scope | Logical boundary (CDE, PHI zone, CUI enclave) | Defines the systems you must prove are isolated |
| Label / filter | Tag or query assigning workloads to scopes | Automates scope membership — reduces drift |
| ADM | Application Dependency Mapping from observed traffic | Live network/data-flow diagram for assessors |
| Workspace | Policy container for one scope or application | Where allow/deny rules are authored |
| Monitor → Simulation → Enforce | Safe rollout sequence | Simulation = change-board evidence before blocking traffic |
| Denied Connections | Log of flows blocked by policy | Primary proof that enforcement operates |

Console areas: Investigate (inventory, flows, vulns) · Defend/Segmentation (policy) · Manage (agents) · Platform (connectors) · Administration (audit log)

Read next: Compliance evidence playbook (full step-by-step) · About CSW (platform intro)

## Universal evidence workflow

Execute these phases for this framework's compliance boundary. Map exports to control IDs in the Reporting & Evidence section below.

| Phase | Goal | Key CSW actions | Typical duration |
| --- | --- | --- | --- |
| 1 — Coverage | Every in-scope workload in CSW | Install agents/connectors; apply compliance labels; create scope | Days 1–10 |
| 2 — Baseline | Machine-generated flow map | Run ADM ≥2 weeks; export clusters; app-owner signoff | Days 11–28 |
| 3 — Policy | Designed isolation before enforce | Build workspace; Simulation mode; fix false positives | Days 29–45 |
| 4 — Operate | Continuous proof between audits | Enforce; quarterly export pack; ADM refresh every 90 days | Ongoing |

### Phase 1 checklist (coverage)

- In-scope host list reconciled to CSW Inventory (100% or documented exceptions)

- Labels applied: compliance:<framework>, data:<classification>, env:<tier>

- CSW scope created matching compliance boundary

- Export: inventory CSV + agent status screenshot

### Phase 2 checklist (baseline)

- ADM running on compliance scope for full business cycle (≥2 weeks)

- Unexpected flows documented (shadow IT, vendor egress, scope creep)

- App owners signed cluster-to-application mapping

- Export: ADM diagram + flow samples with process context

### Phase 3 checklist (policy)

- Default-deny posture defined for sensitive scope

- ADM-imported rules refined; Simulation run ≥1 week

- Change tickets for false-positive fixes; exception register updated

- Export: policy export + simulation report

### Phase 4 checklist (operate)

- Enforcement enabled on pilot scope; negative test recorded in Denied Connections

- Quarterly pack: inventory, policy, denies, vulns, audit log (see playbook)

- SIEM integration verified (sample events)

- Export: enforcement screenshot + quarterly binder

### What CSW evidence does not replace

Physical access, HR/training records, encryption key management, signed BAAs/vendor contracts, formal pen tests, and assessor attestation still require separate programmes. CSW addresses the workload-resident slice: segmentation, flows, process context, vuln reachability, and change drift.

## CSW effectiveness for this framework

- Zones & conduits segmentation on IT-side OT boundaries

- SR control evidence; pair with Cyber Vision/Claroty for device layer

- Jump host and historian path visibility

Compared to manual programmes: static diagrams and annual firewall samples age immediately; CSW ties evidence to live workload behaviour and produces queryable exports on demand — supporting "operating effectively" language in PCI v4.0, SOC 2 CC7, and HIPAA risk analysis.

## 1. Overview

IEC 62443 provides a lifecycle-oriented security framework for industrial automation and control systems. IEC 62443-3-3 specifies foundational requirements (FRs) and associated system requirements (SRs) for IACS components and systems. IEC 62443-2-1 defines requirements for an IACS security management system operated by the asset owner. CSW contributes technical evidence for restricted data flow, access enforcement, integrity-related visibility, detection support, and availability-oriented anomaly awareness on the IT workloads that border or support IACS — not as a substitute for OT protocol inspection or safety-instrumented logic.

### IEC 62443 structure mapped to CSW capabilities

| IEC 62443 topic | Typical artifacts | Relevant CSW capabilities |
| --- | --- | --- |
| FR 5 / SR 5.1–5.4 — Restricted data flow (zones & conduits) | Zone diagrams, conduit allowlists, firewall/ACL rules | Microsegmentation workspaces; scope hierarchy mirroring zones; default-deny with explicit conduits |
| FR 1 / SR 1.1–1.13 — Identification, authentication, access control | Account lifecycle, RBAC, remote access paths | Identity-aware policies (where integrated); least-privilege allowlists; jump-host-only admin paths |
| FR 3 / SR 3.1–3.9 — System & data integrity | Software inventory, patch posture, change detection | Process/binary inventory; listening-port baseline; vulnerability context; drift alerts |
| FR 6 / SR 6.1–6.2 — Event monitoring & timely response | SOC reference designs, timelines, ticket exports | Flow + process forensics; alert correlation inputs to SIEM |
| FR 7 / SR 7.1–7.8 — Resource availability | SLAs, capacity plans, DoS playbooks | Flow anomaly detection (connection/session volume spikes); early warning on saturation patterns |
| 62443-2-1 — Security management / operations | KPIs, dashboards, management review | Continuous inventory/policy dashboards; scheduled evidence export |

Regional or contractual note: Many asset owners implement 62443 requirements through customer purchase specifications or national interpretations. Map this reference design’s SR references to your contractual clauses and audit questionnaires; numbering alone is not sufficient for certification evidence without your target SL and scope.

## 2. Pre-Deployment Checklist

Before deploying CSW sensors on IACS-adjacent IT estates, confirm:

- CSW cluster (SaaS or on-prem) is provisioned; air-gap / data residency rules reviewed if telemetry leaves the plant DMZ

- Network path from workloads to CSW cluster (typically 443 outbound); proxy exceptions documented

- Linux/Windows agent compatibility verified for engineering workstations, jump servers, historians, AD/PKI, and cloud broker VMs

- Cloud connectors configured where plant data lands in AWS / Azure / GCP (historian mirrors, IoT hubs, analytics lakes)

- Stakeholders engaged: OT security lead, plant IT, integrator, SOC, and SMS owner (62443-2-1)

- Maintenance window approved; OT change freeze rules respected — start in Monitoring Only

- PAS / OT tool (Cyber Vision, Claroty, Nozomi) inventory export available for cross-walk of hostnames / VLANs / cell IDs

## 3. Phase 1 — Sensor Deployment (Days 1–5)

### 3.1 On-premises IT adjacent to IACS

Install software sensors on representative tiers: EWS images, jump hosts, historian/MES application servers, AD connectors, vendor VPN concentrators — never on safety PLCs or real-time controllers if those run unsupported or prohibited agent OSes.

# Linux (RHEL/CentOS/Ubuntu family)
sudo rpm -ivh tet-sensor-<version>.rpm    # RHEL/CentOS-compatible
sudo dpkg -i tet-sensor-<version>.deb    # Debian/Ubuntu

# Verify sensor service
sudo systemctl status csw-agent
sudo systemctl enable --now csw-agent

Windows (engineering workstation build):

# Example: install from staged MSI (version/path per release)
msiexec /i "C:\Deploy\tet-sensor-<version>.msi" /qn
Get-Service | Where-Object { $_.Name -like "*tet*" -or $_.Name -like "*csw*" }

Initial posture:

- Enforcement: Monitoring Only (no blocks until ADM + simulation complete)

- Collection: process hash, network flow, listening services, vulnerability exposure (where licensed)

- Tags from day one: zone:<cell>, conduit:<id>, iqs:iacs-adj, sl-target:SL2 (example)

### 3.2 Cloud & hybrid IACS data paths

Use cloud connectors when historian/analytics or IT control plane lives in public cloud:

CSW UI → Platform → External Orchestrators
  → Add AWS / Azure / GCP connector
  → Least-privilege IAM / service principal
  → Enable flow visibility (VPC/VNet flow ingestion where supported)

### 3.3 Sensor validation

CSW UI → Manage → Agents
  → Status: Active for all pilot hosts
  → Confirm telemetry (flow/process) within 15–30 minutes of install
  → Record agent build in baseline export (62443-3 SR 3 / change mgmt input)

## 4. Phase 2 — Scope & Inventory Design — Zones, Conduits, SL (Days 6–12)

### 4.1 Map CSW scopes to IEC zones & conduits

Model scopes to mirror 62443-3-2 zone definitions without renaming your-certified drawings — use labels that reference drawing IDs.

Root: Industrial-Enterprise
├── Plant-<Site>-OT-Support        # IT that touches OT (EWS, jump, historian app tier)
│   ├── Cell-A-Conduit-IT-OT       # Scoped to hosts in conduit endpoints only
│   ├── Cell-B-Conduit-IT-OT
│   └── Shared-Services-IACS       # AD, PKI, patch, backup — constrained to conduits
├── Plant-DMZ-Brokers              # Data diodes / OPC brokers / MQTT gateways (VM-based)
├── Corporate-IT                   # Default no direct path to OT-support
└── Vendor-Remote-Access           # Termination servers for integrator VPN

Conduit rule of thumb: One CSW policy workspace per documented conduit (or group of symmetric conduits) so evidence maps 1:1 to the ZCRD.

### 4.2 Discovery filters for IACS-adjacent candidates

Filter: Historian-MES-Tier
  - Process name contains: historian, mes, opc*, scada, "wonderware"
  - Ports: 1433, 1521, 5432, 135, 502 (context-dependent — validate in YOUR env)
  - Tag pas:ot-adjacent (if synchronized from PAS)

Filter: Jump-EWS
  - Hostname regex: (?i)(ews|eng|hmi-jump|vendor-jump)
  - User workload tag: role=engineering

Validate every automated filter with OT SME sign-off — SR 5 evidence must match the as-engineered conduit list, not a guessed list.

### 4.3 Label strategy (SMS-friendly)

| Label key | Examples | Purpose |
| --- | --- | --- |
| zone | cell-a, line-3 | Aligns to 62443 zone ID |
| conduit | c-ot-to-mes-01 | Audit trail for restricted data flow |
| sl-target | SL2, SL3 | Drive rule strictness / monitoring cadence |
| ics-role | ews, jump, historian, broker | Policy grouping |
| owner | ot-sec, plant-it | Accountability in exports |

## 5. Phase 3 — Application Dependency Mapping & Baseline (Days 13–28)

### 5.1 ADM workspace

ADM establishes observed vs designed conduits — essential for SR 5 and access SR 1 reviews.

CSW UI → Investigate → Application Dependency Mapping
  → New Workspace
  → Name: IACS-Conduit-Baseline-<Site>
  → Scope: Plant-<Site>-OT-Support + DMZ brokers
  → Window: minimum 2–4 weeks (capture patch Tuesday, recipe changes, campaigns)
  → Enable process context; retain ≥ 30 days if storage policy allows

### 5.2 ADM review checklist (62443-oriented)

| Investigation question | SR / FR linkage |
| --- | --- |
| Which corporate subnets talk to historians or OPC brokers? | SR 5 — restricted data flow |
| Are there HTTPS/LD/RDP paths bypassing EWS/jump? | SR 1 — access paths |
| Do EWS images reach the internet directly? | SR 5, SR 1 |
| New binary or service on jump host? | SR 3 — integrity |
| Sudden east-west fan-out from a broker VM? | SR 6 — detection; SR 7 — availability stress |

### 5.3 Baselining for integrity (SR 3 inputs)

Export inventory snapshots after accepted build state:

CSW UI → Investigate → Inventory (or equivalent workload inventory view)
  → Filter: scope = Plant-<Site>-OT-Support
  → Export: processes, packages, listening ports, hashes (as available)
  → Store in secure evidence library with version + timestamp

Repeat on known-good patch cycles to update baseline registers.

## 6. Phase 4 — Policy Design & Enforcement (Days 29–45)

### 6.1 Conduit-aligned policy framework

Translate allowlisted conduits into CSW rules. Example pattern — adjust ports, scopes, and identities to your ZCRD.

Absolute denies (illustrative):

DENY: Corporate-IT → Plant-<Site>-OT-Support (all)
  EXCEPTION: documented Intermediary / jump subnet only

DENY: Vendor-Remote-Access → any except Plant-DMZ-Brokers & Jump hosts

DENY: Plant-<Site>-OT-Support → Internet (0.0.0.0/0)
  EXCEPTION: explicit patch/CDN allowlist + CSW SaaS egress if required

Conduit allows (illustrative):

ALLOW: Plant-DMZ-Brokers ↔ Historian-MES-Tier
  - TCP 135, 49320–49330 (DCOM range — validate), OPC-UA 4840 (if used)

ALLOW: Jump-EWS → Plant-<Site>-OT-Support
  - RDP 3389 / SSH 22 only from Jump-EWS scope

ALLOW: Plant-<Site>-OT-Support → AD-PKI
  - LDAPS 636, Kerberos 88, DNS 53 — block cleartext LDAP 389 where possible

Audit unmatched:

LOG + ALERT: any flow not matching explicit conduit rules

### 6.2 Policy workspace

CSW UI → Defend → Segmentation
  → New Workspace: IEC62443-Conduits-<Site>
  → Import ADM-suggested rules → reconcile with ZCRD
  → Mode: Simulation (minimum 2 weeks typical) → Enforcement by conduit tier

### 6.3 Enforcement progression

| Step | Mode | Objective |
| --- | --- | --- |
| 1 | Simulation | Prove OTSupport apps still function; tune OPC/RPC ranges |
| 2 | Selective enforcement | Lock down highest-risk corporate lateral paths first |
| 3 | Full enforcement on IT border | Default deny except conduits; maintain break-glass procedure |

Integrator coordination: Provide simulation reports before enabling blocks on lines under warranty support.

## 7. Phase 5 — Monitoring, Availability Signals & SMS Feeds

### 7.1 Alerts aligned to 62443 operations

| Alert | Example trigger | SR mapping |
| --- | --- | --- |
| Undocumented conduit attempt | New src→dst across OT-support boundary | SR 5 |
| Cleartext admin | LDAP/HTTP to AD from EWS | SR 1, SR 3 |
| New listening service on jump | Port opens not in baseline | SR 3 |
| Flow anomaly / storm | Connection rate >> baseline | SR 6 (detect), SR 7 (availability) |
| Critical CVE on historian tier | CVSS ≥ threshold | SR 3, 62443-2-1 risk treatment |
| Sensor offline | Loss of heartbeats | SR 6 — visibility gap |

### 7.2 IEC 62443-2-1 continuous monitoring dashboard

Schedule weekly management-visible tiles (exact UI path may vary by release):

- Scope coverage — % of IACS-adjacent IT with active agent

- Policy drift — rules changed since last approval export

- Open simulation violations — unreviewed would-block flows

- Top talkers across conduits — compare to PAS asset roles

Export snapshots into your SMS review record monthly minimum.

## 8. Control-by-control mapping — Framework requirement → CSW → evidence

Use this table to start questionnaire mapping. Official conformity assessment requires your SL-T, scope statement, and test methods from the certification body or customer spec.

### 8.1 SR 5 — Restricted data flow (zones & conduits)

| IEC 62443-3-3 requirement (summary) | CSW capability | Evidence produced |
| --- | --- | --- |
| SR 5.1 — Segmentation / zones | Scope hierarchy; segmentation workspaces; labels zone, conduit | Scope export; diagram cross-walk memo |
| SR 5.2 — Segmentation for zones of differing security requirements | Tiered scopes by SL labels; stricter workspaces for higher SL | Policy diff between SL scopes |
| SR 5.3 — Conduit control | Allowlist rules per conduit; default deny | Policy JSON/export + simulation/enforcement logs |
| SR 5.4 — Covert channel mitigation (as applicable at IT layer) | Egress restrictions; anomaly detection on volume | Flow anomaly reports + change tickets |

### 8.2 SR 1 — Identification, authentication, and access control

| IEC 62443-3-3 requirement (summary) | CSW capability | Evidence produced |
| --- | --- | --- |
| SR 1.1–1.13 (human / process / service access paths) | Identity-aware policies (when integrated); admin path lock-down; least privilege allowlists | Flow logs with user/process context; policy allow/deny history |
| Remote access paths via jump | Rules limiting src to jump scope; deny corporate→OTSupport direct | ADM + enforcement hit logs |

### 8.3 SR 3 — System integrity

| IEC 62443-3-3 requirement (summary) | CSW capability | Evidence produced |
| --- | --- | --- |
| SR 3.1–3.9 (software integrity, malware deterrence inputs, etc.) | Process & binary inventory; package visibility; vulnerability data | Inventory export; drift alerts; VA connectors / built-in reports |
| Unauthorized software indicators | New process / listener alerts vs baseline | Ticket + before/after inventory |

### 8.4 SR 6 — Event monitoring & timely response

| IEC 62443-3-3 requirement (summary) | CSW capability | Evidence produced |
| --- | --- | --- |
| SR 6.1 — Audit logging support | Flow + process retention; export APIs / UI exports | Raw & summary logs with UTC stamps |
| SR 6.2 — Continuous monitoring inputs | Alerts; SIEM forwarders | Alert rule catalog; SOC ingest proof |

### 8.5 SR 7 — Resource availability

| IEC 62443-3-3 requirement (summary) | CSW capability | Evidence produced |
| --- | --- | --- |
| SR 7.1–7.8 (DoS considerations at system level) | Flow volumetrics; session rate anomalies; saturation precursors | Time-series anomaly exports + IR narrative |

### 8.6 IEC 62443-2-1 — Security management system (technical contributors only)

| 62443-2-1 theme (summary) | CSW capability | Evidence produced |
| --- | --- | --- |
| Operations monitoring & KPIs | Dashboards; scheduled exports | Monthly PDF/CSV appendices to SMS review |
| Incident response support | Forensic drill exports | Tabletop package — flow + process trace |

## 9. Vulnerability, patch & compensating controls

### 9.1 Vulnerability visibility

CSW UI → Investigate → Vulnerability Report
  → Scope: Plant-<Site>-OT-Support
  → Filter: CVSS ≥ 7.0 (example)
  → Export CSV for SMS risk register linkage

### 9.2 Compensating controls when patching waits for outage

- Narrow allow rules to known peer scopes only

- Raise alert severity on vulnerable process names

- Capture full flow logs to affected workload until patched

## 10. Forensics & incident reconstruction

CSW UI → Investigate → Flow Search
  → Time range: incident window (extend for long-running OT campaigns)
  → Source/Destination: suspected broker or EWS
  → Export: CSV/JSON with process + user context

CSW UI → Investigate → Process Search
  → Parent/child chain for suspicious binaries on jump hosts

Retain exports per your SMS / legal hold policy; correlate with PAS PCAP or ICS alerts for full OT picture.

## 11. Audit preparation & evidence export

### 11.1 Quarterly evidence pack (adjust to customer cadence)

| Evidence item | CSW source | Typical IEC mapping |
| --- | --- | --- |
| Conduit policy export | Defend → workspace export | SR 5.x |
| Simulation vs enforcement history | Policy lifecycle / audit log | SR 5, SR 1 |
| ADM cluster report | ADM workspace | SR 5, SR 1 |
| Inventory baseline delta | Inventory exports | SR 3.x |
| Vulnerability exposure | Vulnerability report | SR 3, 62443-2-1 |
| Alert & flow excerpts | Flow Search, Alerts | SR 6, incident packs |
| Coverage report | Agent inventory | 62443-2-1 monitoring scope |

### 11.2 Bash helper examples (on analysis workstation)

After UI export to /evidence/csw/:

# Verify exported policy archive integrity (after UI download)
shasum -a 256 /evidence/csw/iec62443-policy-export-YYYYMMDD.zip | tee /evidence/csw/SHA256SUMS

# Redact non-production subnets before sharing with integrator
perl -pe 's/\b10\.\d{1,3}\.\d{1,3}\.\d{1,3}\b/10.REDACTED.0.0/g' \
  /evidence/csw/flows-incident-window.csv > /evidence/csw/flows-incident-window-redacted.csv

## 12. Boundaries — what CSW does not cover

- Level 0–2 OT devices (PLCs, IEDs, devices without supported agents) — use PAS/OT security tools; CSW does not inspect proprietary fieldbus payloads at wire speed.

- Safety instrumented functions — CSW is not a SIL-rated safety device; engineering lifecycle evidence stays with SIS vendor tools.

- Physical security & personnel screening — access badges, gates, contractor vetting — outside CSW.

- Cryptographic key management policy — CSW may enforce paths (e.g., TLS-only) but does not replace PKI governance or HSM decisions.

- 62443-2-1 organizational processes — CSW supplies telemetry and policy exports; it does not author your procedures, training roster, or supplier security clauses.

## 13. Common pitfalls

| Pitfall | Mitigation |
| --- | --- |
| Mis-mapping CSW scopes to electrical zones instead of cyber zones | Anchor labels to approved cyber ZCRD IDs |
| Blocking dynamic RPC/OPC ranges without ADM | Long simulation + integrator test scripts |
| Deploying only on corporate IT | OT-adjacent IT is the compliance-critical tier |
| Ignoring cloud shadow IT paths to plant data | Enable cloud connectors for mirrored historians |
| Expecting CSW to replace OT IDS | Maintain Cyber Vision / Claroty / Nozomi for ICS context |

## Related Frameworks

- NERC CIP — analogous IT/OT boundary evidence pattern for BES entities.

- NIST SP 800-82 — operational technology companion guidance (external).

- ISO/IEC 27001:2022 — when plants pair 62443 with enterprise ISMS audits.

- NIST SP 800-207 — zero trust patterns for conduit enforcement narratives.

- UK NCSC CAF v3.2 — zones and conduits are the reuse path for CAF B5 on the IT side of an IT/OT boundary.

### Appendix A — Sample segmentation policy fragment (illustrative YAML-style)

Do not paste verbatim into production. Replace scopes, addresses, and L4 tuples with values from your ZCRD. Syntax mirrors conceptual CSW rule metadata; exact API/UI format follows product version.

workspace: IEC62443-Conduits-Site01
mode: simulation          # change to enforcement after sign-off
default_action: deny
rules:
  - name: conduit-opcua-historian
    action: allow
    src_scope: Plant-DMZ-Brokers
    dst_scope: Historian-MES-Tier
    services:
      - tcp/4840
  - name: admin-via-jump-only
    action: allow
    src_scope: Jump-EWS
    dst_scope: Plant-Site01-OT-Support
    services:
      - tcp/22
      - tcp/3389
  - name: log-unknown-east-west
    action: alert
    src_scope: Plant-Site01-OT-Support
    dst_scope: Plant-Site01-OT-Support
    match: not_in_conduit_allowlist

### Appendix B — PAS correlation workflow

- Export asset list from Cyber Vision / Claroty / Nozomi (IP, MAC, VLAN, firmware).

- Join on IP or hostname with CSW inventory.

- Flag CSW-only or PAS-only assets — resolve before SR 5 attestation.

- For discrepancies, field-verify with plant engineering.

Document prepared for industrial account engagements. Replace site names, drawing references, and SL targets with customer-specific values before delivery.